## Slide 1
Module A14 – Sphere Training Package 2015
What is it and how can it be implemented?
Sphere technical chapter on water supply, sanitation and hygiene promotion (WASH)

## Slide 2: Problems in Water Supply, Sanitation & Hygiene Promotion (WASH)
Irish Aid photo
ICRC photo

## Slide 3: Problem 1: Lack of water
In large scale emergencies, particularly those resulting in mass displacement, there simply isn’t enough water readily available.
Tommaso Della Longa/IFRC
Notes: Picture caption: Lebanon November 2014 - Lebanese Red Cross water distribution (20000 litres) for Syrians in "New camp“.

## Slide 4: What’s wrong with this picture?
If this pump can deliver 2 m3 of water per day, how many people can it adequately serve if there is no other source of water available?
A. If you assume 15 l/p/d… 133 people.
Q. Why?
Photo - www.lifewater.ca/kardia.htm
Notes: 2 m3 is equal to 2,000 litres of water by definition. 2,000 litres divided into 15 litres minimum per person equals 133.3 people…. So say 133.

## Slide 5: Visualising water quantities
1 metre
1 metre
1 metre
1 cube of 10 cm x 10 cm x 10 cm =1 litre
10 cm
10 cm
1 m3 of water = 1 metric ton
1 litre of water = 1 kg
1 m3 of water = 1,000 litres
1 m3 of water = 1,000 kg

## Slide 6: Problem 2: Water unsafe to drink
In many disasters where enough water is readily available, it isn’t safe to drink.
Katherine Mueller, IFRC
Notes: Picture caption: Brakna region, Mauritania, April 2013.

## Slide 7: All surface water is considered to be contaminated
IFRC/Marko Kokic

## Slide 8: Problem 3: Poor emergency water distribution systems
Emergency water distribution systems, especially for camps, are often badly designed for ongoing, daily use.
Long queues for water are common…
So are constant repairs
OXFAM photo
OXFAM photo

## Slide 9: Equipment for an emergency water system
Choose the best equipment for a rural emergency camp’s water system from the selection below.
Tap A
Tap B
Tap C
Water Carrier A
Water Carrier B
Water Carrier C
Notes: Like many technical questions…. The answer depends a bit on the context and the notion of “best for whom?” The pros and cons for the taps shown and the water containers are listed below.
Taps…
Simple screw valve tap with rubber washers. These are cheap and therefore often ordered to save money or because they are immediately available. Also everyone know how to fix them. However, they are almost always designed for household use, which is far below the constant use experienced in a large camp setting. Therefore, these taps are often broken, dripping, and inappropriate for heavy continuous use. Since the screw-down design requires the user to shut the tap off each time, they are often left running… resulting in waste of a precious resource.
Spring-loaded valve tap. These are good since they will automatically close by the integral spring in the tap, avoiding the problem described above of the running tap left open by the last user. However, the springs on these will eventually become weak, meaning that they too leak before long.
This is a gravity tap. The heavy weighted tap closes the valve by gravity. The tap is operated by lifting the weight, when the hand is removed the valve closes…. And gravity never wears our, so it is a long-lasting device made for heavy continuous use. However, these are more expensive, must be specially ordered, and in some cases (when the weight was made of brass) the value of the metal made them good targets for theft as they could be resold for scrap metal (newer ones are made of heavy plastic and other metals of less value).
Water Containers….
Rectangular jerry can – perfect for daily use, relatively cheap, strong and durable. However, once contaminated they can be hard to clean, and they are bulky for shipping. The small mouth make them better for keeping clean as children cannot put their hands inside.
This collapsible jerry can is great for packing into trucks and aeroplanes making delivery to emergency sites much easier and more efficient. However, the designs are often weak, and quickly break. The type shown also has a separate handle which will quickly break, making the container very difficult to carry. Some newer versions have an integral handle moulded into the form of the collapsible container, making them much stronger.
Open bucket. This is often very useful for the families as multi-purpose containers, however, the open top makes the susceptible to splashing, waste, and pollution. Buckets with close-fitting lids can be a good option.
Whichever container is chosen, the size should be manageable by those carrying them (i.e. often women and children).

## Slide 10: Problem 4: Drainage, Drainage, Drainage!
Camp Hope, June 14, 1999
Camp Hope, June 22, 1999

## Slide 11: Selecting a tent camp site
Which hectare (A-L) of this site is most suitable for a tent camp, based on site slope only?
0m 100m 200m 300m 400m
A
B
C
D
I
J
K
L
E
F
G
H
610
620
630
610
610
+ 619
Tree cover
Elevation in 2m increments
Building
Paved road
Intermittent stream
River
Marsh
Notes: To do this exercise, the participants must know how to calculate slope and read a contour map. This may be too much for short session without previous exposure to the basic concepts. However, for the right group this could work. The key points and the answer are listed below.
Site slope should be between 1% and 5% according to Sphere. Slope is the measurement of the amount of increase in elevation (vertical distance) across a given run (horizontal distance). Generally, this is measured in meters increase in elevation over a (horizontal) run of 100 meters. It is expressed as a percentage….i.e. so many meters change in altitude over 100 meters distance across the ground.
One hectare is defined as 10,000 m2. So, a square that is 100 meters on each side measures 1 hectare by definition. The grid on the map shown is divided into 1 hectare squares, so the measure across each square on the grid is 100 meters.
A contour map, like the one shown, indicates the height above sea level (usually in meters) by use of contour lines drawn on the map (usually brown lines so they are not misunderstood to be roads or streams). The map legend will explain what interval each contour line measures. In this case each contour line represents a change of 2 meters in altitude.
Analysis – Hectares E and K are likely the best sites based purely on slope since in each case a person walking across the square would cross (or nearly reach) 2 contours lines, which means an increase in elevation of 4 meters (2 lines at 2 meters change each). Since the grid is 100 meters, that means a change of 4 meters in altitude across a run of 100 meters, or 4% slope – just right per the Sphere guidance. Of these 2 choices, K is the better choice as it has good road access, and is not cut off by the river in case of flooding.

## Slide 12: Problem 5: People defecation in inappropriate locations
In mass population emergencies involving displacement to crowded areas, people defecation in inappropriate locations might quickly contaminate the site.
Red Cross Society of Côte d'Ivoire/IFRC
Notes: Photo caption: Côte d’Ivoire. 2013. In many villages, volunteers helped communities create sanitation maps that help understand and pinpoint health concerns, such as places of open defecation, water sources or livestock pens, as part of the revolutionary 'community-led total sanitation' project.

## Slide 13: Problem 6: Garbage piles
Garbage piles attract rats and flies which pose serious threats to public health.

## Slide 14: Problem 7: Underused latrines
Often, even when there are enough latrines provided, they are not used.
Why?
Patrick Fuller, IFRC
Notes: The answer to this is social and psychological rather than engineering-based. Generally speaking, when latrines are for public rather than private or family use, there is no one to clean and maintain them as their own. Therefore they quickly become smelly, nasty, and unusable. This can be controlled if dedicated cleaners are part of the concept.
Photo caption: Typhoon Haiyan, Philippines. 2014. The typhoon destroyed over 500,000 homes leaving survivors living in temporary shelters with no access to adequate sanitation. The Red Cross has built community latrines that are maintained by locals such as Minerva Aguilar. San Roque Barangay, Tanouan, Eastern Leyte.

## Slide 15: VIP latrines are a world-wide standard…
Zimbabwe
Mexico
Dominican Republic
Pakistan

## Slide 16: Ventilated Improved Pit (VIP) Latrine
See ‘Appropriate and adequate toilet facilities’, pages 107- 109 in 2011 edition
in use
Removable hole cover
Vent pipe
Fly screen!
Dark inside
UNHCR/e-Centre/InterWorks - Emergency Management Training

## Slide 17: Vector control
Basically:
Reduce vectors through waste management and site drainage
Prevent mosquito bites through provision of bednets
Use chemicals only with expert guidance and always with extreme caution

## Slide 18: Problem 8: Recontamination of clean water
Ika Koeck/IFRC
In large scale emergencies, particularly those resulting in mass displacement, there simply isn’t enough water readily available.
Notes: Caption: Kelantan. Malaysia, 2015. The villagers of Kampung Pasir Tumboh have been using water from the river to clean their houses and household items.

## Slide 19: What’s wrong with this picture?
Notes: It seems from the photograph that no distribution of jerry cans has been made. People are in line with whatever they can find to carry water. Open buckets are vulnerable to contamination, and some re-used containers may be dangerous if the previous contents contained toxic chemicals, cleaners, or pesticides, for example.

## Slide 20: Problem 9: Sanitation needs overwhelmed
The scope, scale, and speed of the emergency situation overwhelms sanitation needs.
BBC photo

## Slide 21: The relationships between the components of the Sphere handbook

## Slide 22: Visualising the indicators…
Irish Aid photo
ICRC photo

## Slide 23: Hygiene Promotion
  Key risks are identified
  Programmes include mechanisms for participation
  All groups have safe and equitable access
  WASH staff communicate clearly and can answer community questions
  There is a system in place for maintenance and management
(page 89 of the 2011 Edition)
Q. How many hygiene promoters/community mobilisers should be provided in a camp situation?
A. Two hygiene promoters/community mobilizers per 1,000 members of the affected population (page 93)
Notes: Sphere Guidance Note 5 on page 93 explains…. “…there should be two hygiene promoters/community mobilizers per 1,000 members of the affected population.”

## Slide 24: Hygiene items
  Everyone has access to hygiene items (soap, water containers)
  Women and girls of menstruating age are provided with appropriate menstrual hygiene items based on consultations about appropriate materials
  Everyone has access to information and training
(page 94 of the 2011 Edition)
Q. How much soap should be provided per person in a camp situation?
A. 250g/month (page 95)
Notes: Sphere Guidance Notes #1, under ‘List of basic hygiene items’ on page 95 explains that 250g of bathing soap and 200g of laundry soap should be provided each month.

## Slide 25: Water supply
  Average of 15 litres of water per person per day
  Maximum distance from any household to nearest water point 500 meters
  Queuing time no more than 30 minutes
(page 97 of the 2011 Edition)

## Slide 26: Water supply
The maximum distance from any shelter to nearest water point is 500 meters
R = 500m
There is at least 1 water point for 250 people*
(page 99 of the 2011 Edition)

## Slide 27: Water supply
“Average use is at least 15 litres of water per person per day”
  So… 20,000 people would need 20,000 x 15 litres = 300,000 litres per day.
  This amounts to a storage container of 300 m3
  Which is a cube of water 6m x 7m x 7m.

## Slide 28: What does this mean for planning and programming?
300 m3 =… 10 x 30,000 litre bladder tanks or
30 x 10 m ton water tankers

## Slide 29: Issues to investigate for evaluation
What issues or questions must you investigate about this situation if you want to evaluate the project using the Sphere Project Humanitarian Charter and Minimum Standards in Humanitarian Response?
Photo: Rachel Stabb/ OXFAM
Notes: To analyse this situation, the assessors need to know:
Total population using the tap (to find persons/tap and litres/person)
Queuing time at the tap stand
Quality of the water in the tank
Refilling rate and annual fluctuations in water available in the tank – is it trucked here, diverted from springs or streams, or pumped from a well?
Input from the community in the siting and accessibility of the tank and tapstand – were they consulted?
Photo caption: children from Dos Puertas, El Salvador drawing water from newly installed tapstands. (Tank behind is 10,000 litre capacity.) Part of earthquake emergency response.

## Slide 30: Water tanks – typical sizes, volumes
Assuming these tanks can each be filled once daily, how many people can each tank support in an emergency camp?
Assume working volume to be 90% of nominal volume.
Nominal storage capacities
10,500 litres
45,000 litres
70,000 litres
95,000 litres
2.5 m
6.4 m
2.3 m
1.5 m
2.3 m
3.0 m
Notes: This one is just calculation:
10,500 l @ 90% = 9,450 l. 9,450 l divided by 15 l/p/d = 630 people
45,000 l @ 90% = 40,500 l. 40,500 l divided by 15 l/p/d = 2,700 people
70,000 l @ 90% = 63,00 l. 63,000 l divided by 15 l/p/d = 4,200 people
95,000 l @ 90% = 85,500 l. 85,500 l divided by 15 l/p/d = 5,700 people

## Slide 31: Some Sphere water quality indicators
  No faecal coliforms per 100ml at delivery point
  Residual free chlorine @ 0.5 mg per litre
  Turbidity below 5 NTU
  No outbreaks of water-related disease
(page 100 of the 2011 Edition)
Q. What does all of that mean?
Notes: All of this means that the water at the point of delivery to the users should be clean and free from contamination by faecal matter (no faecal coliform bacteria such as e-coli). The water should also be treated with chlorine to kill bacteria so that the indicator above can be reached. Additionally, enough chlorine must remain active in the water, after the initial disinfection, to continue killing new bacteria that may be re-introduced into the water by children, or others using the water.
Turbidity is simply a measure of how cloudy (dirty) the water is. It should be relatively clear and without sediment or other materials suspended in the water that will reduce the ability of the chlorine to disinfect the water.
Finally, the real indicator of success is that there are no outbreaks of water-borne diseases amongst the community.

## Slide 32: E. coli
E. coli are bacteria, full name is Escherichia Coli

## Slide 33: Nephelometric Turbidity Units (NTUs)
NTUs are the units we use when we measure Turbidity.
The term Nephelometric refers to the way the instrument estimates how light is scattered by suspended particulate material in the water.
This measurement generally provides a very good correlation with the concentration of particles in the water that affect clarity.
http:// lake access.org/russ/turbidity.htm

## Slide 34: Turbidity
Comparative examples of effect of varying NTUs from different causes
http://lake access.org/russ/turbidity.htm

## Slide 35: Some water use facilities indicators
  2 containers for water collection of 10-20 litres each per household (narrow neck and or cover)
  1 water storage vessel of 20 litres per household (narrow neck and or cover)
  Separate bathing cubicles for men and women (where communal)
  1 clothes washing basin per 100 people where communal (provide separate private laundering areas for women only)

## Slide 36: What’s right, What’s wrong? Why?
Afghan children collect water from a hand pump in the Naser Bagh refugee settlement in Peshawar, Pakistan
Locally available, 20-litre plastic jerry cans
UNICEF photo: S. Noorani
CDC photo
Notes: The water pump in the photograph looks well constructed and maintained. The plastic buckets provided have tight lids and are of a convenient size for carrying. However, the old bucket nearby is also likely used as a drinking water container and can be easily recontaminated by the users.
The jerry can at the right is a good design and has a hygiene note printed on the container.

## Slide 37: Design, layout, purchasing or installation of components
  Emergency tanker
  Bladder tank
  Tapstand
What Sphere key indicators would apply in the design, layout, purchasing or installation of these components?
Notes: All of the Sphere indicators in the WASH chapter would apply in principle, however the key ones to watch for in the physical design of this system are those related to Water Supply (page 97).

## Slide 38: Some Sphere excreta disposal key indicators
  Environment is free from human faeces
  Maximum 20 people per toilet
  Use by households or segregated by sex
  No more than 50m from dwellings
  Latrines and soakaways (in most soils) are at least 30m away from any groundwater source, and bottom of pits at least 1.5m above water table.
waterdot.org

## Slide 39: Explain this picture – what does it tell you?
If there are 35,000 people in this camp, how many latrines are needed?
Where do you put them in the camp?
New Shamshatoo Camp, Peshawar, Pakistan, August, 2001
InterWorks photo
Notes: The uniform tents tell us that a programme of response for this camp has been undertaken already. The brick latrines (actually VIP design) tells us that the camp has been here for some time and that the planners believe that the population may be here for some time to come. Finally, the individual design (not public) of the latrines probably indicates that these units are built on a per/family basis.
Following the guidance to provide one latrine per family where possible, the answer would be to divide the total population figure of 35,000 people by the average family size. If 7 people/family, for example, the camp would need approximately 5,000 latrines.
If this number was unattainable, the rule to provide at least 1 latrine for every 20 people could be used. The result would be 35,000 people divided by 20 people/latrine = 1,750 latrines needed.

## Slide 40: Some layout, accessibility and vector control indicators

50 m
100 m
Trash Bin
Per each 10 households
Latrine
Communal Garbage Dump/Pit
2011 Sphere Edition
1-2 km from malarial breeding sites

## Slide 41: Some Sphere solid waste indicators
  All households have access to a refuse container and are no more than 100 meters from a communal refuse pit.
  One 100 litre refuse container is available for every 10 families, where domestic waste is not buried on site.
InterWorks photo

## Slide 42: Some Sphere site drainage indicators
  Areas around dwellings and water points are kept free of standing wastewater, and stormwater drains are kept clear.
  Shelters, paths and water and sanitation facilities are not flooded or eroded by water.
Kabul, Afghanistan, 2003
InterWorks photos

## Slide 43: Conclusions
  WASH
  Hygiene promotion
  Water supply
  Excreta disposal
  Vector control
  Solid waste management
  Drainage

## Slide 44: Remember!
The Humanitarian Charter, the Core Humanitarian Standard and the technical chapters should always come together.
Notes: Ask participants to reflect for a minute and finally to share in plenary what message this image is sending.
Conclude by saying that the technical chapters should always be used in conjunction with the Humanitarian Charter, the Protection Principles and the Core Humanitarian Standard (the latter replacing Sphere Core Standards 'Chapter).